Introduction

Ib = design current

In = Protective/fuse rating breaker size

Iz = Cable rating

NOTE: I stands for current. Ib In and Iz are all current based.

Simple example:

- Heater has a design current of 5

- needs to have a fuse of 6

- and a cable rating of 7.2.

Tutor aside: Always have leeway when it comes to Ib, In and Iz. For example, it says “less than or equal to”. make sure it is always greater than. As shown in this example.

Ib​ – Design current: The actual current that the load is expected to draw under normal operation.

In​ – Nominal current: of the protective device: The rated current of the circuit breaker or fuse (e.g., a 16 A MCB).

Iz​ – Current-carrying capacity:(ampacity) of the cable or conductor, under the given installation conditions.

START FIRST PRACTISE

Question:

If we run a cable in a 30 degree room.

With a Twin and Earth 70 degrees.

Grouped with 7 cables with 320mm insulation

And a 32 A breaker.

Workings out:

Ib = design current

In = Protective/fuse rating breaker size

Iz = Cable rating

The first step is to calculate the design current => Ib.

Ib = ??

The second step is to calculate the breaker size => In

In =  32 A breaker.

The third step is to calculate Iz => cable rating;

- The pre-requisite is to calculate It => current carrying capacity.

- The base formula to deduce It =>  current carrying capacity.

Ca => ambient temperature

- Ca - The ambient temperature is deduced as 1 from Table F1 on page 168.

Cg => grouping

- Cg - is deduced as 0.71. Because there are seven cables in the wall. So this additional cable makes 8.

Ci => thermal insulation

- Ci - is deduced as 0.51. Because the question states “320mm insulation” which, when rounded up to 400. Corresponds to 0.51 Derating factor (Ci ).

Cf => account for 3036 fuse box

- Cf - is deduced as 1. As the on guide site states “for all other devices Cf = 1. ”

In => represents the current at which the protective device is designed to operate in order to protect the circuit from damage.

- In  - The question gives us the breaker size as 32 A

Therefore It ,

END FIRST PRACTISE

START SECOND PRACTISE

Question:

In is 45. The total answer is 63.

A shower is running through 100mm insulation. Which has a 70 degree thermoplastic cover. The cable is fitted into an enclosed wall with 6 circuits. The shower requires 7.2 kW to run and uses 230 volts.

The temperature of the bathroom is 25 degrees.

Finally, Sam’s fuse box has not been updated in a while and is version 3036.

Workings out:

- Ib = design current

- In = Breaker Size

- Iz = cable rating

The first step is to calculate the design current => Ib.

- To calculate the design current (Ib) we use the PIV formula triangle;

- The answer for Ib will be measured in amps.

PIV formula triangle

- I = P / V or

- Current = Power / Voltage;

- 7.2 kW / 230 volts = 31.30 amps.

- 7,200 / 230 = 31.30 A

Diversity rule check

- For Ib  (the design current) check if the appliance appears on table A1 on page 136;

- If yes, apply the diversity calculation;

- In this instance a shower does not appear on the table;

- So Ib = 31.30 amps.

The second step is to calculate the breaker size => In

- To calculate In read the Header row on Table B1 (page 140);

- We must calculate the right sized breaker to use;

- The design current (Ib) has been calculated as 31.30 amps - as deduced in the first step;

- Round up to the nearest value in the header row table Table B1 (page 140);

- From the table we can conclude that the right breaker size is 45 A for a design current  (Ib) of 31.30 amps;

- 30 A and 20 A are too small. 60 A is too large

- Note that we highlighted “protective device is a semi-enclosed fuse to BS 3036”

The third step is to calculate Iz => cable rating;

- To calculate Iz => cable rating;

- We must first calculate It => current carrying capacity .

It  => current carrying capacity formula

- The above formula is used to calculate It;

- From It we can deduce the value of Iz;

- Use page 167 to calculate Ca, Cg, Ci and Cf

Ca => ambient temperature

- Calculate Ca first;

- We know that the Ambient template is 25 degrees and the insulation is 70 degrees;

- Hence, in Table F1 on page 168 the answer is 1.03.

Cg=> grouping

- We calculate Cg because of the Table F3 on page 170;

- The question states 6 cables already situated into the wall;

- Therefore this additional cable will make it seven.

Ci => thermal insulation

- Ci is deduced from Table F2 on page 169;

- Ci - factors in how insulation around a cable can affect its ability to dissipate heat and thus impact on the maximum amount of current that it can safely carry;

- The text informs us that the length of the insulation is 100mm this equates to 0.78.

Cf => account for 3036 fuse box

- Cf is deduced from page 167 at the bottom of the page;

- The answer is 0.725;

- This number is deduced from the text “a semi-enclosed fuse to BS 3036”.

In => represents the current at which the protective device is designed to operate in order to protect the circuit from damage

- In has been deduced from the second step to be 45 A;

- Because, we deduced the breaker size (In) based on the design current (Ib);

- If the current exceeds 45 A then the breaker device will operate.

It = 143.1A

IZ - Cable size. We need a cable size that can carry a 143.1 A current flow.

As mentioned in the question. We already have 6 circuits. With this addition, there will be 7 circuits.

END SECOND PRACTISE

Voltage drop

Introduction

Zs = Ze + (R1+R2)

Zs = Earth Fault Loop Impedance (EFLI)

Ze = Connection from fuse box back to transformer

(R1+R2) = Line + CPC resistance. Internal from the circuit to the fuse box

R1 = Live

R2 = Earth

Z = Impedance

(R1 + R2)

Question

Working out

= 0.22 Ω

=> Zs = Ze + (R1 + R2)

=> 0.22 + 0.09

=> 0.31 Ω

230 / 0.31 = 741.94 A (will flow in an event of a fault)