## Slide 1
Resistivity
Unit 202: Principles of electrical science

## Slide 2
Resistance – length of conductor
LM = L1 + L2 + L3 + L4
RT = R1 + R2 + R3 + R4
R | ∝ | L

## Slide 3
EXAMPLE 1. If a cable has a resistance of 0.15/m what will be the resistance of 320m of the same cable?
Since resistance is proportional length:
Resistance | = | Ω/m × length
 | = | 0.15 × 320
 | = | 48Ω
Resistance – length of conductor

## Slide 4
EXAMPLE 2. If 50m of a conductor have a resistance of 0.01 what would be the resistance of 500m of the same cable?
Since resistance is proportional length:
Resistance | = | new length × resistance old length
 | = | 0.1Ω
Resistance | = | 500 × 0.01 50
Resistance – length of conductor

## Slide 5
EXAMPLE 3. If 750m of a conductor have a resistance of 0.013 what will be the resistance of 150m of the same conductor?
Since resistance is proportional length:
Resistance | = | new length × resistance old length
 | = | 0.0026Ω
Resistance | = | 150 × 0.013 750
Resistance – length of conductor

## Slide 6
aT = a1 + a2 + a3 + a4
R | ∝ | 1 a
 | 1 | = | 1 | + | 1 | + | 1 | + | 1 | 
 | RT |  | R1 |  | R2 |  | R3 |  | R4 | 
Resistance is inversely proportional to area
Resistance – cross sectional area of conductor

## Slide 7
EXAMPLE 4. If the resistance of 100m of a certain conductor is 0.076, calculate the resistance of 100m of the same conductor but with:
a) Since R is ∝ to 1/a, then:
R | = | 0.076 ÷ 2
 | = | 0.038Ω
a) twice the CSA
b) four times the CSA
c) half the CSA
d) one quarter of the CSA.
Resistance – cross sectional area of conductor

## Slide 8
b) Since R is ∝ to 1/a, then:
R | = | 0.076 ÷ 4
 | = | 0.019Ω
Resistance – cross sectional area of conductor
c) Since R is ∝ to 1/a, then:
R | = | 0.076 ÷ 1/2
 | = | 0.152Ω
d) Since R is ∝ to 1/a, then:
R | = | 0.076 ÷ 1/4
 | = | 0.304Ω

## Slide 9
EXAMPLE 5. If the resistance of 100m of a certain conductor is 1.24, calculate the resistance of 500m of the same conductor but with twice the CSA.
But:
Resistance | = | new length × resistance old length
 | = | 6.2Ω
Resistance | = | 500 × 1.24 100
R | ∝ | 1 a | (therefore the resistance must be halved)
 | = | 3.1Ω
R | = | 6.2 2
Resistance – cross sectional area of conductor

## Slide 10
Material | Resistivity at 20°C
Copper | 17.2 × 10-9 ohm metre
Aluminium | 26.5 × 10-9 ohm metre
Silver | 15.9 × 10-9 ohm metre
Gold | 22.4 × 10-9 ohm metre
Brass (58% copper) | 59.0 × 10-9 ohm metre
Brass (63% copper) | 71.0 × 10-9 ohm metre
Resistivity – type of conducting material

## Slide 11
or
Where:
R = conductor resistance in ohms
ρ = cable resistivity in Ω m
L = cable length in metres
a = cross sectional area (CSA) in metre2.
Resistivity

## Slide 12
EXAMPLE 6. Calculate the resistance of 1,000m of 16mm2 (CSA) single copper conductor. Take  to be 17.2 x 10-9  metre.
Resistivity – cross sectional area of conductor

## Slide 13
EXAMPLE 6. Calculate the resistance of 1,000m of 16mm2 (CSA) single copper conductor. Take  to be 17.2 x 10-9  metre.
 | = | 17.2 × 10-9 × | 1,000 | 
 |  |  | 16 x 10-6 | 
 | = | 1.075Ω
Resistivity – cross sectional area of conductor

## Slide 14
EXAMPLE 7. Calculate the resistance of an aluminium wire 100m long and CSA of 25mm2. Take the resistivity of aluminium to be 26.5 x 10-9  metre.
Resistivity – cross sectional area of conductor

## Slide 15
EXAMPLE 7. Calculate the resistance of an aluminium wire 100m long and CSA of 25mm2. Take the resistivity of aluminium to be 26.5 x 10-9  metre.
R | = | ρ x | L | 
 |  |  | a | 
 | = | 26.5 x 10-9 x | 100 | 
 |  |  | 25 x 10-6 | 
 | = | 0.106Ω
Resistivity – cross sectional area of conductor

## Slide 16
EXAMPLE 8. Calculate the resistance of 100m of copper conductor if  = 17.2 x 10-9  metre for the material and the CSA is 2.5mm2.
Resistivity – cross sectional area of conductor

## Slide 17
EXAMPLE 8. Calculate the resistance of 100m of copper conductor if  = 17.2 x 10-9  metre for the material and the CSA is 2.5mm2.
R | = | ρ x | l | 
 |  |  | a | 
 | = | 17.2 x 10-9 x | 100 | 
 |  |  | 2.5 x 10-6 | 
 | = | 0.688Ω
Resistivity – cross sectional area of conductor

## Slide 18
EXAMPLE 9. Calculate the resistance of 100m of silver conductor if  = 15.9 x 10-9  metre for the material and the CSA is 2.5mm2.
Resistivity – cross sectional area of conductor

## Slide 19
EXAMPLE 9. Calculate the resistance of 100m of silver conductor if  = 15.9 x 10-9  metre for the material and the CSA is 2.5mm2.
R | = | ρ x | l | 
 |  |  | a | 
 | = | 15.9 x 10-9 x | 100 | 
 |  |  | 2.5 x 10-6 | 
 | = | 0.636Ω
Resistivity – cross sectional area of conductor

## Slide 20
As we have demonstrated in this lesson, the conductors themselves will have resistance and, like any resistance will affect the current flow and voltage drop in the circuit. The magnitude of the volt drop will not only depend on the resistance of the cable but also the amount of current being drawn by the load.
Voltage drop

## Slide 21
Example 10
A load with a resistance of 23 is connected to 230V supply with a cable that has a total resistance of 0.7. Calculate:
The voltage drop in the cable,
The voltage that will appear across the load.
Voltage drop

## Slide 22
Example 10
A load with a resistance of 23 is connected to 230V supply with a cable that has a total resistance of 0.7. Calculate:
The voltage drop in the cable,
The voltage that will appear across the load.
Voltage drop

## Slide 23
Example 10
A load with a resistance of 23 is connected to 230V supply with a cable that has a total resistance of 0.7. Calculate:
The voltage drop in the cable,
The voltage that will appear across the load.
Voltage drop

## Slide 24
The End
Unit 202: Principles of electrical science