## Slide 1
Cooker circuits and diversity
Unit 203: Electrical installations technology

## Slide 2
Cooker circuits

## Slide 3
Example 1. Calculate the assumed demand for a 230 volt cooker which contains:
2 x 1.0kW hob plates
2 x 2.0kW hob plates
1 x 2.0kW oven/grill
1 x 3.0kW oven.
 | Maximum current | = |  | 
Maximum total power | = | 
 | = | kW
 |  | = |  | 
Maximum current | = | A
Cooker circuits

## Slide 4
Example 1. Calculate the assumed demand for a 230 volt cooker which contains:
2 x 1.0kW hob plates
2 x 2.0kW hob plates
1 x 2.0kW oven/grill
1 x 3.0kW oven.
 | Maximum current | = | P | 
 |  |  | V | 
Maximum total power | = | (2 x 1) + (2 x 2) + 2 + 3
 | = | 11kW
 |  | = | 11 x 1,000 | 
 |  |  | 230 | 
Maximum current | = | 47.83A
Cooker circuits

## Slide 5
The first 10A at 100% | = | 10A
Leaving 37.83 at 30% | = | 11.35A
Total | = | 21.35A
This means that the cable supplying this cooker would have to have a rating of at least 21.35A. If the control unit contained a socket outlet then the rating would have to be at least 26.35A.
The assumed current demand, allowing for diversity, is:
Cooker circuits

## Slide 6
The End
Unit 203: Electrical installations technology