## Slide 1
Conduit systems
Unit 203: Electrical installations technology

## Slide 2
Three main types:
metal (steel)
PVC
flexible.
Conduit systems

## Slide 3
Advantages:
affords conductors good mechanical protection
permits easy rewiring
minimises fire risks
can be utilised as the circuit protective conductor.
Disadvantages:
under certain conditions, moisture is liable to form on the inside of the conduit
expensive compared with some other systems
liable to corrosion when subject to acid, alkali and other fumes.
Steel conduit systems

## Slide 4
Types of steel conduit finish:
galvanised for outdoors or situations where steam or dampness is present.
black enamelled for general work in dry situations.
Typical sizes (diameters):
16mm
20mm
25mm
32mm
available in 3.75 metre lengths.
Steel conduit systems

## Slide 5
Steel conduit systems

## Slide 6
Specialist steel conduit tools
Bending machine
Formers
Stocks and dies
Steel conduit systems

## Slide 7
Advantages:
light in weight and easy to handle
easy to saw, cut and clean
simple to form and bend
does not require painting
minimal condensation due to low thermal conductivity in walls
speed of erection
excellent electrical and fire resistant properties.
Disadvantages:
care must be taken when gluing joints to avoid forming a barrier across the inside of the conduit
if insufficient adhesive is used the joints may not be waterproof
pvc expands around five times as much as steel and this expansion must be allowed for.
PVC conduit systems

## Slide 8
Types of PVC conduit:
Heavy Gauge Super High Impact: Designed to withstand arduous site conditions and extreme weather conditions. Major building contractors and government departments often specify this type of conduit for use.
Light Gauge Super High Impact: Suitable for pre-cast and in situ concrete work.
Heavy Gauge Standard Impact: Suitable for typical conduit installations.
Heavy Gauge High Temperature Material: Suitable for installations where 80/85°C temperatures are expected.
Typical sizes:
16, 20, 25, 32, 38 and 50mm diameter
in 3 metre lengths.
PVC conduit systems

## Slide 9
PVC conduit systems

## Slide 10
Short straight runs
Sizing conduit systems

## Slide 11
Long straight runs or runs with bends
Sizing conduit systems

## Slide 12
Example 1. The following cables are to be drawn into a straight 2m length of conduit:
2 off solid core 1.5mm2
4 off solid core 2.5mm2
4 off stranded 4mm2.
Calculate the conduit size required to accommodate these cables.
Sizing conduit systems

## Slide 13
Example 1. The following cables are to be drawn into a straight 2m length of conduit:
2 off solid core 1.5mm2
4 off solid core 2.5mm2
4 off stranded 4mm2.
Calculate the conduit size required to accommodate these cables.
Cable factors from Table E1 (On-Site Guide)
2 off solid core 1.5mm2 | = | 27 x 2 | = | 54
4 off solid core 2.5mm2 | = | 39 x 4 | = | 156
4 off stranded 4mm2 | = | 58 x 4 | = | 232
Cable factors total | = | 54 + 156 + 232 | = | 442
From On-Site Guide Table E2, size required | = | 20mm
Sizing conduit systems

## Slide 14
Example 2. The following cables are to be drawn into a 2m length of conduit with 2 bends:
2 off solid core 1.5mm2
4 off solid core 2.5mm2
4 off stranded 4mm2.
Calculate the conduit size required to accommodate these cables.
Sizing conduit systems

## Slide 15
Example 2. The following cables are to be drawn into a 2m length of conduit with 2 bends:
2 off solid core 1.5mm2
4 off solid core 2.5mm2
4 off stranded 4mm2.
Calculate the conduit size required to accommodate these cables.
Cable factors from Table E3 (On-Site Guide)
2 off solid core 1.5mm2 | = | 22 x 2 | = | 44
4 off solid core 2.5mm2 | = | 30 x 4 | = | 120
4 off stranded 4mm2 | = | 43 x 4 | = | 172
Cable factors total | = | 44 + 120 + 172 | = | 336
From On-Site Guide Table E4, size required | = | 25mm
Sizing conduit systems

## Slide 16
The End
Unit 203: Electrical installations technology