## Slide 1
Cable selection
Unit 203: Electrical installations technology

## Slide 2
The size of a cable to be used for an installation depends upon:
the current rating of a cable under defined installation conditions
the maximum permitted drop in voltage, as defined by BS7671 Section 525 with values in Appendix 4, section 6.4
satisfying earth fault loop impedance requirements specified in BS7671 Regulation Tables 41.2, 41.3 and 41.4.
Cable selection

## Slide 3
The factors which influence the current rating are the:
design current, Ib – the cable must carry the full load current
type of cable – PVC, MIMS, copper conductors or aluminium conductors
installed conditions – eg clipped to the surface or installed with other cables in trunking
surrounding temperature – cable resistance increases as temperature increases and insulation may melt if the temperature is too high
type and size of protection – for how long will the cable have to carry fault current?
Cable selection

## Slide 4
Current carrying capacity
In order to comply with BS 7671, the following relationship must be complied with:
Ib ≤ In ≤ Iz
where: Ib = design current of circuit
In = rated current or current setting of protective device
Iz = current carrying capacity of a cable for continuous service under the particular installation conditions concerned
and
It ≥ Iz
where: It = tabulated current carrying capacity of a cable.
Cable selection

## Slide 5
Steps to be taken when determining the cable size.
Determine the design current (Ib) of the circuit. This should be the value after applying any applicable factors for diversity.
Select the type and current rating of the protective device, which must be equal to or larger than the design current (In).
Determine the various correction factors applicable and apply them to the protective rating.
Determine the installation method to be used.
Select the cable from the current carrying capacity tables in Appendix 4 of BS 7671.
Cable selection

## Slide 6
A number of correction factors are available to take into account various installation conditions. These are as follows:
Ca ambient or surrounding temperature correction factor which is given in Tables 4B1 and 4B2 of BS7671 Appendix 4
Cc for circuits buried directly in the ground or in a duct in the ground Cc = 0.9 (Appendix 4 section 5.1). For cables installed above ground Cc = 1
Cd for depth of burial correction factor, which is given in Table 4B4 of BS7671 Appendix 4
Cf where the protective device is a semi-enclosed fuses to BS3036, Cf = 0.725, otherwise Cf = 1 (Appendix 4 section 5.1)
Cg grouping correction factor given in Tables 4C1 to 4C6 of BS7671 Appendix 4
Cable selection

## Slide 7
Ci correction factor to be used when cables are enclosed in thermal insulation. BS7671 Regulation 523.9 gives three possible correction values:
where a cable is installed in a thermally insulated wall or above a thermally insulated ceiling, the cable being in contact with a thermally conductive surface on one side, current carrying capacities are tabulated in Appendix 4
where the cable is totally surrounded over a length greater than 0.5m, a factor of 0.5 must be applied
where the cable is totally surrounded over a short length less than 0.5m, the appropriate factor given in Table 52.2 of BS7671 should be applied
Cable selection
Cs for thermal resistivity of soil correction factor, which is given in Table 4B3 of BS7671 Appendix 4.

## Slide 8
Example 1. A 6.5kW, 230V shower unit is to be wired in a domestic bathroom some 18m away from the mains consumer unit. A general purpose thermoplastic PVC insulated and sheathed flat twin with cpc cable will be clipped to the side of the 100mm ceiling joists over much of its length with one other similar cable in a roof space which, it is anticipated, will reach 35°C in the summer and where thermal insulation is installed up to the top of the joists. Assuming a TN‑S supply, calculate the minimum cable size to carry the current if the circuit is to be protected by:
A semi-enclosed fuse to BS3036
a Type B CB to BS EN 60898.
Cable selection

## Slide 9
 | Design current, Ib | = | Power | 
 |  |  | Volts | 
 |  | = | 6,500W | 
 |  |  | 230V | 
 |  | = | 28.26 amperes
a) | Current setting of protection, In | = | 30A (next size up from 28.26A)
Cable selection

## Slide 10
Ca ambient temperature; the correction factor for 35C is 0.94 from Table 4B1of Appendix 4.
Cc cable is installed above ground so Cc = 1.
Cd as the cable is installed above ground, this factor does not apply.
Cf the protection is by a semi-enclosed fuse and, therefore, a factor of 0.725 must be applied.
Cg the cable is grouped with one similar cable so we have a factor of 0.8 from Table 4C1 of Appendix 4.
Ci thermal insulation is in contact with one side of the cable and therefore current carrying capacities are tabulated in Appendix 4.
Cs as the cable is installed above ground, this factor does not apply.
Cable selection

## Slide 11
 | Cable rating, Iz | = | 30 | 
 |  |  | (0.94 x 1 x 0.725 x 0.8) | 
 |  | = | 55A
The installation method is from Table 4A2 Reference Method 100.
From Column 2 of Table 4D5 a 16mm2 cable, having a rating (It) of 57 amperes, is required to carry this current.
Cable selection
 | Cable rating, Iz | = | In | 
 |  |  | (Ca x Cc x Cf x Cg) | 

## Slide 12
Now test for volt drop. The maximum permissible volt drop is 5% of the nominal supply voltage:
 | Maximum volt drop | = | 5 x 230 | 
 |  |  | 100 | 
 |  | = | 11.5V
From Table 4D5 Column 8 the volt drop per ampere metre for a 16mm2 cable is 2.8mV. Therefore, the volt drop for this cable length and load is equal to:
Voltage drop | = | 2.8 x 10-3 x 28.26 x 18
 | = | 1.42V
Since this is less than the maximum permissible value of 11.5 volts, a 16mm2 cable satisfies the current carrying capacity and voltage drop requirements, and is therefore the chosen cable when semi-enclosed fuse protection is used.
Cable selection

## Slide 13
b) | Current setting of protection, In | = | 32A (next size up from 28.26A)
Ca ambient temperature; the correction factor for 35C is 0.94 from Table 4B1 of Appendix 4.
Cc cable is installed above ground so Cc = 1.
Cd as the cable is installed above ground, this factor does not apply.
Cf since protection is by a CB, the factor is 1
Cg the cable is grouped with one similar cable so we have a factor of 0.8 from Table 4C1 of Appendix 4.
Ci thermal insulation is in contact with one side of the cable and therefore current carrying capacities are tabulated in Appendix 4.
Cs as the cable is installed above ground, this factor does not apply.
Cable selection

## Slide 14
 | Cable rating, Iz | = | 32 | 
 |  |  | (0.94 x 1 x 1 x 0.8) | 
 |  | = | 42.6A
The installation method is from Table 4A2 Reference Method 100.
From Column 2 of Table 4D5 a 10mm2 cable, having a rating (It) of 45 amperes, is required to carry this current.
Cable selection
 | Cable rating, Iz | = | In | 
 |  |  | (Ca x Cc x Cf x Cg) | 

## Slide 15
From Table 4D5 Column 8 the volt drop per ampere metre for a 10mm2 cable is 4.4mV. Therefore, the volt drop for this cable length and load is equal to:
Now test for volt drop. The maximum permissible volt drop is 5% of the nominal supply voltage.
Voltage drop | = | 4.4 x 10-3 x 28.26 x 18
 | = | 2.24V
Since this is less than the maximum permissible value of 11.5 volts, a 10mm2 cable satisfies the current carrying capacity and voltage drop requirements, and is therefore the chosen cable when circuit breaker type B protection is used.
Cable selection

## Slide 16
The End
Unit 203: Electrical installations technology