## Slide 1: Initial verification
PowerPoint presentation
Unit 304: Electrical Installations: inspection, testing and commissioning

## Slide 2: Initial verification
When a new installation is completed it should be inspected and tested and this is covered in Chapter 61 (page 197) of BS7671 where it is referred to as ‘initial verification’.
It is recommended that the condition of an existing installation be inspected and tested periodically and this is covered in Chapter 62 (page 203) of BS7671 where it is referred to as ‘periodic inspection and testing’.

## Slide 3: Inspection
Initial verification
The inspection should verify that the installation (BS7671 Regulation 611.2 - page 197)
Installed electrical equipment is of the correct type and complies with applicable British Standards or acceptable equivalents.
The fixed installation is correctly selected and erected.
The fixed installation is not visibly damaged or otherwise defective.

## Slide 4: Inspection
Periodic inspection and testing
The inspection should verify that the installation provides for (BS7671 Regulation 621.2 – page 203)
safety of persons and livestock against the effects of electric shock and burns
protection against damage to property by fire and heat arising from an installation defect
confirmation that the installation is not damaged or deteriorated so as to impair safety
the identification of installation defects and departures from the requirements of these Regulations that may give rise to danger.

## Slide 5: Inspection
Preparing for inspection
Make contact with client.
Arrange isolation timings.
Agree the range and limitations of inspection.
Gather information (details of client, previous test results and certificates).
Carry out a risk assessment.
Prepare safe system of work including PPE requirements.

## Slide 6: Inspection
Information to be made available to the person or persons carrying out the inspection and testing:
The results of the assessment of the fundamental principles (Section 131 – page 16)
Maximum demand and diversity (Section 311 – page 43)
Conductor arrangement and system earthing (Section 312 – page 43)
Supplies (Section 313 – page 47)
Diagrams and documentation (Regulation 514.9.1 – page 121)
Guidance Note 3 Chapter 2 Section 2.3 Required information (page 17) expands on the information required.

## Slide 7
Any questions?